TECHNICAL SPECIFICATION

- Definitions and abbreviations

  - Buyer shall mean “Energijos skirstymo operatorius”, AB.

  - Supplier shall mean an undertaking – natural entity, private legal entity, public legal entity, other organizations and their subdivisions or a group of such entities, who is a party to the Contract concluded with the Buyer.

  - Contract shall mean the Contract concluded by the Supplier and the Buyer regarding the Object of the Procurement.

  - Goods shall mean 0.4 kV electrical parameter meters with remote data reading via the GSM network.

  - Order shall mean a document for supply of the Goods submitted by the Buyer to the Supplier specifying names, quantities of the Goods, delivery addresses, and the time limit.

- Object OF THE Procurement

0.4 kV electrical parameter meters with remote data reading via the GSM network.

- SCOPES OF THE Object OF THE Procurement

9 sets.

- Place of implementation of the contractual obligations

Delivery of the Goods in the territory of the Republic of Lithuania. Specific destination point for delivery of the ordered Goods would be indicated at the time of placing the Order by sending to the e-mail address indicated in the Contract.

- REIKALAVIMAI PIRKIMO OBJEKTUI

Technical requirements for 0.4 kV electrical parameter meter with remote data reading via GSM network are described in Table 1.

Table 1

| No. | Value | Requirement | Parameters |
| --- | --- | --- | --- |
| 1. | Pajungimas/ Connection | 1.1. Tipas/Type; 1.2. Įtampa/Voltage; 1.3. Srovė/Current; | 1.1. 4 laidų/3 fazės (3P4W) / 4 wires, 3 phases (3P4W); 1.2. Krokodiliniai gnybtai/ alligator clamps; 1.3. Rogovskio ritė su atvira kilpa arba jai lygiavertė 3 fazėms, 60 cm / Rogowski coil with an open loop or an equivalent thereof, 60 cm for 3 phases. |
| 2. | Įtampa/Voltage | 2.1. Vardinė darbo įtampa Un/Nominal operating voltage Un; 2.2. Darbinės įtampos ribos/Operating voltage range; 2.3. Vardinis dažnis/Nominal frequency; | 2.1. 3x230/400 V; 2.2. 0,5xUn … 1,15xUn; 2.3. 50 Hz; |
| 3. | Srovė/Current | 3.1. Matuojama srovė In/ Measurable current In | 3.1. Turi gebėti matuoti 500 A ir didesnę apkrovos srovę / Must be able to measure 500 A and higher load current. |
| 4. | Registruojami parametrai/ Registered parameters | 4.1. Įtampa/Voltage; 4.2. Srovė/Current; 4.3. Aktyvi galia/Active power; 4.4. Pilnutinė galia/ Apparent power; 4.5. Galios koeficientas./Power factor; 4.6. Aktyvi energija/Active energy; | 4.1. RMS, maksimali momentinė reikšmė/maximum instantaneous value, kryptis ir viršįtampis/direction and surge, dažnis/frequency; 4.2. RMS, maksimali momentinė reikšmė/maximum instantaneous value, perkrova/overload; 4.3. Kiekvienai fazei individualia/by each phase, bendra/total; 4.4. Kiekvienai fazei individualia/by each phase, bendra/total; 4.5. Absoliuti reikšmė/absolute value, induktyvinė/inductive, talpuminė/capacitive; 4.6. Kiekvienai fazei individualia/by each phase, visa/total, kryptis/direction, apkrovos profilis/load profile. |
| 5. | Standartai/ Standards | 5.1. Sertifikatai/Certification; 5.2. Tikslumo klase/precision class; | 5.1. CE; 5.2. B pagal EN 50470-3 arba jam lygiavertį/ B according to EN 50470-3 or an equivalent thereof |
| 6. | Duomenų perdavimas/data transfer | 6.1. Sąsaja/interface; 6.2. Duomenų tipas/data type | 6.1. Standatinio dydžio SIM kortelės lizdas GSM/GPRS ryšiui/Standard size SIM card holder for GSM/GPRS connection; 6.2. Matavimai/measurements, laiko sinchronizavimas/time sync, |
| 7. | Registratoriaus konstrukcija/ Structure of the meter | 7.1. Gabaritai/Dimensions LxWxH; 7.2. Svoris/Weight; 7.3. Korpusas/enclosure; 7.4. Išorinės jungtys/External connections; | 7.1. Ne didesni gabaritai nei/ no bigger dimensions than 225x85x70 mm; 7.2. ≤ 500 g.; 7.3. Atmosferos poveikiui atsparus plastikas arba jam lygiavertė medžiaga/weather-proof plastic or an equivalent material; 7.4. 3 jungtys, skirtos rogovskio ritėms/ 3 connectors for Rogowski coils |
| 8. | Darbinės sąlygos/ Operating conditions | 8.1. IP apsaugos klasė/ IP protection class; 8.2. Darbinė temperatūra/ Operating temperature; | 8.1. Ne mažiau kaip IP 67 (įrenginio korpusas, jungtys, rogovskio ritės)/ No less IP 67 (enclosure of the device, connectors, rogowski coils); 8.2. Nuo -35ºC iki +35ºC arba platesnės ribos / -From 35ºC to +35ºC or a wider range; |
| 9. | Registratoriaus duomenų peržiūra/ Meter data visualization | 9.1. Registratorių elektriniai parametrai kaupiamajame debesyje/Electrical parameters of the meters are stored in the cloud; 9.2. Duomenys į debesį per GSM tinklą atnaujinami realiu laiku ≤ 5 sec. intervalais/ Data is updated on the cloud in real time via the GSM network every ≤ 5 seconds; 9.3. Debesyje turi būti galimybė vizualiai peržiūrėti elektrinius parametrus/ The cloud must be equipped with an option allowing to visually view all electrical parameters; 9.4. Debesyje turi būti galimybė kurti atskiras vartotojų paskyras, kiekvienai paskyrai priskiriant individualius registratorius/ The cloud must be equipped with an option allowing to create new user accounts assigning individual meters to each account; |  |
| 10. | Debesies licencija/Cloud licence | 10.1. Kiekvienas registratorius turi turėti ne trumpesnę nei 3 m. licenciją naudotis debesies platforma/ Every meter must be provided with a licence for using the cloud platform for a period of at least 3 years. |  |
| 11. | Garantija/Warranty | 11.1. Ne trumpesnė nei 2 metai/ No less than 2 years |  |

- procedure and deadlines for implementation of the contractual obligations

  - The Goods must be new, not used before.

  - The Goods would be purchased in accordance with a written Order placed by the Buyer during the validity period of the Contract. The Supplier would be required to deliver the Goods to the address indicated in Paragraph 4 of this Technical Specification during the Buyer’s business hours (I-IV 07:30 a.m. – 04:30 p.m., V 07:30 a.m. – 03:15 p.m.).

  - The Buyer would place the Order to the Buyer by sending it to the e-mail address indicated in the Annex to the Special Part of the Contract.

  - The Goods must be delivered no later than within 7 (seven) calendar days since the date of placing the Order to the Supplier.

  - The Supplier would be required to deliver the Goods by using one’s own resources, staff, facilities, and equipment.

  - The risk of accidental loss or damage of the Goods shall fall on the Supplier of the Goods until the Goods are delivered to the destination point.

- quality and elimination of shortcomings

  - A warranty period shall be established for the Goods by the manufacturer of the Goods, which shall be at least 2 (two) years long counting from the signing date of the Certificate of Acceptance – Transfer of the Goods.

  - A time limit of 10 (ten) calendar days shall be established for elimination of shortcomings noticed at the time of transfer – acceptance of the Goods or during the warranty period.

7.3.  The Supplier would be required to eliminate the shortcomings noticed at the time of transfer – acceptance of the Goods or during the warranty period.

- documents to be submitted along with the delivered goods

  - Acceptance – Transfer Certificate and VAT Invoice.